## Instructions
Instructions and guidelines for use of M&E sheet
1 | The monitoring and evaluation (M&E) excel consists of one sheet per pump station
2 | Each pump station sheet consists of all proposed recommendations
3 | Firstly, the base case detailed and key performance indicator (KPI) along with annual energy consumption is presented
4 | A post implementation case is presented, which calculated the KPI and annual energy consumption
5 | The user is recommended to fill data in only the light green highlighted cells
6 | Other cells are locked and can't be accessed by the user

## Summary Sheet
Consolidated summary
S.No. | Name of Pump Station | Energy Conservation Measure | Baseline |  | Implementation case |  | Savings
|  |  | Energy consumption | KPI | Energy consumption | KPI | Energy saving | KPI improvement | GHG reduction
|  |  | kWh/year | kWh/m3 | kWh/year | kWh/m3 | kWh/year | % | kgCO2-e
1 | Borderline | Replacement of transfer pump | 25881 | 0.20437 | 18184.5757 | 0.14198 | 7696.4243 | 30.5269 | 5.0796
2 |  | Replacement of borepump-4 with efficient pump | 104257 | 0.36454 | 78825.1194 | 0.28083 | 25431.8806 | 22.9635 | 16.785
3 |  | Replacement of FTL with LED tube lights | 264 | NA | 63 | NA | 201 | 76.1364 | 0.13266
4 | Skyline | Installation of VFD on transfer pumps | 109396 | 0.26827 | 104835.2072 | 0.25373 | 4560.7928 | 5.4222 | 3.0101
5 |  | Replacement of borepump-1 with efficient pump | 139534.3 | 0.53302 | 107307.8027 | 0.41003 | 30180.2747 | 23.0734 | 19.919
6 |  | Replacement of borepump-3 with efficient pump | 166639 | 0.87588 | 120355.721 | 0.5695 | 46283.279 | 34.9796 | 30.547
7 |  | Replacement of FTL with LED tube lights | 264 | NA | 63 | NA | 201 | 76.1364 | 0.13266
8 | Tasahe | Replacement of borepump-2 with efficient pump | 104992 | 0.428 | 68265.6412 | 0.23526 | 34394.4173 | 45.0335 | 22.7003
9 |  | Replacement of borepump-4 with efficient pump | 78653 | 0.74964 | 55309.5399 | 0.46806 | 23343.4601 | 37.5626 | 15.4067
10 |  | Replacement of FTL with LED tube lights | 264 | NA | 63 | NA | 201 | 76.1364 | 0.13266
11 | Titinge | Installation of VFD on transfer pumps | 158038 | 0.32969 | 151669.4061 | 0.32155 | 6368.5939 | 2.4709 | 4.2033
12 |  | Replacement of borepump-2 with efficient pump | 107486 | 0.45949 | 78341.5046 | 0.41435 | 27293.9646 | 9.8233 | 18.014
13 |  | Replacement of borepump-4 with efficient pump | 68700 | 0.4975 | 64448.7268 | 0.48642 | 4251.2732 | 2.2264 | 2.8058
14 |  | Replacement of FTL with LED tube lights | 264 | NA | 63 | NA | 201 | 76.1364 | 0.13266
15 | Tuvaruhu JICA | Replacement of transfer pump with IE4 & VFD | 323788 | 0.61787 | 218235.5784 | 0.40117 | 105552.4216 | 35.0724 | 69.6646
16 |  | Replacement of borepump-1 with efficient pump | 64841 | 0.31331 | 53506.25 | 0.20942 | 10615.0496 | 33.1588 | 7.0059
17 |  | Replacement of borepump-3 with efficient pump | 92248 | 0.27815 | 57316.68 | 0.15395 | 34931.32 | 44.6509 | 23.0547
18 |  | Replacement of FTL with LED tube lights | 44 | NA | 15.75 | NA | 28.25 | 64.2045 | 0.018645
19 | Tuvaruhu SIWA | Replacement of transfer pump with IE4 & VFD | 132548 | 0.26016 | 97588.2311 | 0.18887 | 34959.7689 | 27.4013 | 23.0734
20 |  | Replacement of borepump-4 with efficient pump | 99911 | 0.27891 | 67555.5807 | 0.15527 | 32355.4193 | 44.3291 | 21.3546
21 |  | Replacement of FTL with LED tube lights | 55 | NA | 21 | NA | 34 | 61.8182 | 0.02244
22 | Kwaibala | Replacement of transfer pump | 70873 | 0.33992 | 44991.7104 | 0.2158 | 25881.2896 | 36.5137 | 17.0817
23 |  | Replacement of FTL with LED tube lights | 66 | NA | 21 | NA | 45 | 68.1818 | 0.0297

## Borderline PS
Borderline Pump Station
ECM-1: Replacement of transfer pump |  |  | ECM-2: Replacement of borepump-4 with efficient pump |  |  | ECM-3: Replacement of FTL with LED tube lights
Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value
Baseline |  |  | Baseline |  |  | Baseline
Operating flow | m3/h | 34.3 | Operating flow | m3/h | 36.1 | FTL light rating | W | 36
Discharge head | m | 33 | Overall head | m | 59.7 | Ballast rating | W | 8
Power input | kW | 7.01 | Power input | kW | 13.16 | Number of lights | no's. | 24
Net daily water duty | m3 | 350.889 | Net daily water duty | m3 | 769 | Total rating | kW | 1.056
Specific energy consumption | kWh/m3 | 0.20437 | Specific energy consumption | kWh/m3 | 0.36454 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 25881 | Annual energy consumption | kWh/year | 104257 | Annual energy consumption | kWh/year | 264
Implementation case |  |  | Implementation case |  |  | Implementation case
Water flow rate | m3/h | 64 | Water flow rate | m3/h | 32 | LED tube light rating | W | 21
Power input | kW | 9.087 | Power input | kW | 8.9866 | No. of lights | no's. | 12
Specific energy consumption | kWh/m3 | 0.14198 | Specific energy consumption | kWh/m3 | 0.28083 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 18184.5757 | Annual energy consumption | kWh/year | 78825.1194 | Annual energy consumption | kWh/year | 63
Energy saving | kWh/year | 7696.4243 | Energy saving | kWh/year | 25431.8806 | Energy saving | kWh/year | 201
KPI improvement | % | 30.5269 | KPI improvement | % | 22.9635 | KPI improvement | % | 76.1364
GHG emission reduction | tCO2-e | 5.0796 | GHG emission reduction | tCO2-e | 16.785 | GHG emission reduction | tCO2-e | 0.13266

## Skyline PS
Skyline Pump Station
ECM-1: Installation of VFD on transfer pumps |  |  | ECM-2: Replacement of borepump-1 with efficient pump |  |  | ECM-3: Replacement of borepump-3 with efficient pump |  |  | ECM-4: Replacement of FTL with LED tube lights
Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value
Baseline |  |  | Baseline |  |  | Baseline |  |  | Baseline
Operating flow | m3/h | 78.8 | Operating flow | m3/h | 31.8 | Operating flow | m3/h | 17 | FTL light rating | W | 36
Discharge head | m | 62 | Overall head | m | 96.9 | Overall head | m | 129.7 | Ballast rating | W | 8
Power input | kW | 21.14 | Power input | kW | 16.95 | Power input | kW | 14.89 | Number of lights | no's. | 24
Net daily water duty | m3 | 1132 | Net daily water duty | m3 | 717 | Net daily water duty | m3 | 579 | Total rating | kW | 1.056
Specific energy consumption | kWh/m3 | 0.26827 | Specific energy consumption | kWh/m3 | 0.53302 | Specific energy consumption | kWh/m3 | 0.87588 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 109396 | Annual energy consumption | kWh/year | 139534.3 | Annual energy consumption | kWh/year | 166639 | Annual energy consumption | kWh/year | 264
Implementation case |  |  | Implementation case |  |  | Implementation case |  |  | Implementation case
VFD frequency set | Hz | 43.27 | Water flow rate | m3/h | 29.9 | Water flow rate | m3/h | 24.1 | LED tube light rating | W | 21
Water flow rate | m3/h | 56.3243 | Power input | kW | 12.26 | Power input | kW | 13.725 | No. of lights | no's. | 12
Power input | kW | 14.291 | Specific energy consumption | kWh/m3 | 0.41003 | Specific energy consumption | kWh/m3 | 0.5695 | Operating hours | hour/year | 250
Specific energy consumption | kWh/m3 | 0.25373 | Annual energy consumption | kWh/year | 107307.8027 | Annual energy consumption | kWh/year | 120355.721 | Annual energy consumption | kWh/year | 63
Annual energy consumption | kWh/year | 104835.2072 | Energy saving | kWh/year | 30180.2747 | Energy saving | kWh/year | 46283.279 | Energy saving | kWh/year | 201
Energy saving | kWh/year | 4560.7928 | KPI improvement | % | 23.0734 | KPI improvement | % | 34.9796 | KPI improvement | % | 76.1364
KPI improvement | % | 5.4222 | GHG emission reduction | tCO2-e | 19.919 | GHG emission reduction | tCO2-e | 30.547 | GHG emission reduction | tCO2-e | 0.13266
GHG emission reduction | tCO2-e | 3.0101

## Tasahe PS
Tasahe Pump Station
ECM-1: Replacement of borepump-2 with efficient pump |  |  | ECM-2: Replacement of borepump-4 with efficient pump |  |  | ECM-3: Replacement of FTL with LED tube lights
Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value
Baseline |  |  | Baseline |  |  | Baseline
Operating flow | m3/h | 32.5 | Operating flow | m3/h | 13.9 | FTL light rating | W | 36
Overall head | m | 70.26 | Overall head | m | 103 | Ballast rating | W | 8
Power input | kW | 13.91 | Power input | kW | 10.42 | Number of lights | no's. | 24
Net daily water duty | m3 | 795 | Net daily water duty | m3 | 518 | Total rating | kW | 1.056
Specific energy consumption | kWh/m3 | 0.428 | Specific energy consumption | kWh/m3 | 0.74964 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 104992 | Annual energy consumption | kWh/year | 78653 | Annual energy consumption | kWh/year | 264
Implementation case |  |  | Implementation case |  |  | Implementation case
Water flow rate | m3/h | 33.1 | Water flow rate | m3/h | 21.6 | LED tube light rating | W | 21
Power input | kW | 7.787 | Power input | kW | 10.11 | No. of lights | no's. | 12
Specific energy consumption | kWh/m3 | 0.23526 | Specific energy consumption | kWh/m3 | 0.46806 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 68265.6412 | Annual energy consumption | kWh/year | 55309.5399 | Annual energy consumption | kWh/year | 63
Energy saving | kWh/year | 34394.4173 | Energy saving | kWh/year | 23343.4601 | Energy saving | kWh/year | 201
KPI improvement | % | 45.0335 | KPI improvement | % | 37.5626 | KPI improvement | % | 76.1364
GHG emission reduction | tCO2-e | 22.7003 | GHG emission reduction | tCO2-e | 15.4067 | GHG emission reduction | tCO2-e | 0.13266

## Titinge PS
Titinge Pump Station
ECM-1: Installation of VFD on transfer pumps |  |  | ECM-2: Replacement of borepump-2 with efficient pump |  |  | ECM-3: Replacement of borepump-4 with efficient pump |  |  | ECM-4: Replacement of FTL with LED tube lights
Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value
Baseline |  |  | Baseline |  |  | Baseline |  |  | Baseline
Operating flow | m3/h | 77.8 | Operating flow | m3/h | 27.4 | Operating flow | m3/h | 28 | FTL light rating | W | 36
Discharge head | m | 87.5 | Overall head | m | 65.98 | Overall head | m | 92.3 | Ballast rating | W | 8
Power input | kW | 25.65 | Power input | kW | 12.59 | Power input | kW | 13.93 | Number of lights | no's. | 24
Net daily water duty | m3 | 1292.3 | Net daily water duty | m3 | 518 | Net daily water duty | m3 | 363 | Total rating | kW | 1.056
Specific energy consumption | kWh/m3 | 0.32969 | Specific energy consumption | kWh/m3 | 0.45949 | Specific energy consumption | kWh/m3 | 0.4975 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 158038 | Annual energy consumption | kWh/year | 107486 | Annual energy consumption | kWh/year | 68700 | Annual energy consumption | kWh/year | 264
Implementation case |  |  | Implementation case |  |  | Implementation case |  |  | Implementation case
VFD frequency set | Hz | 43.67 | Water flow rate | m3/h | 21.6 | Water flow rate | m3/h | 15.1 | LED tube light rating | W | 21
Water flow rate | m3/h | 56.8258 | Power input | kW | 8.95 | Power input | kW | 7.345 | No. of lights | no's. | 12
Power input | kW | 18.272 | Specific energy consumption | kWh/m3 | 0.41435 | Specific energy consumption | kWh/m3 | 0.48642 | Operating hours | hour/year | 250
Specific energy consumption | kWh/m3 | 0.32155 | Annual energy consumption | kWh/year | 78341.5046 | Annual energy consumption | kWh/year | 64448.7268 | Annual energy consumption | kWh/year | 63
Annual energy consumption | kWh/year | 151669.4061 | Energy saving | kWh/year | 27293.9646 | Energy saving | kWh/year | 4251.2732 | Energy saving | kWh/year | 201
Energy saving | kWh/year | 6368.5939 | KPI improvement | % | 9.8233 | KPI improvement | % | 2.2264 | KPI improvement | % | 76.1364
KPI improvement | % | 2.4709 | GHG emission reduction | tCO2-e | 18.014 | GHG emission reduction | tCO2-e | 2.8058 | GHG emission reduction | tCO2-e | 0.13266
GHG emission reduction | tCO2-e | 4.2033

## Tuvaruhu JICA PS
Tuvaruhu JICA Pump Station
ECM-1: Replacement of transfer pump with IE4 motor & VFD |  |  | ECM-2: Replacement of borepump-1 with efficient pump |  |  | ECM-3: Replacement of borepump-3 with efficient pump |  |  | ECM-4: Replacement of FTL with LED tube lights
Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value
Baseline |  |  | Baseline |  |  | Baseline |  |  | Baseline
Operating flow | m3/h | 62.1 | Operating flow | m3/h | 24.8 | Operating flow | m3/h | 38.9 | FTL light rating | W | 36
Discharge head | m | 107 | Overall head | m | 39.9 | Overall head | m | 30.12 | Ballast rating | W | 8
Power input | kW | 38.37 | Power input | kW | 7.77 | Power input | kW | 10.82 | Number of lights | no's. | 4
Net daily water duty | m3 | 1490.4 | Net daily water duty | m3 | 700 | Net daily water duty | m3 | 1020 | Total rating | kW | 1.056
Specific energy consumption | kWh/m3 | 0.61787 | Specific energy consumption | kWh/m3 | 0.31331 | Specific energy consumption | kWh/m3 | 0.27815 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 323788 | Annual energy consumption | kWh/year | 64841 | Annual energy consumption | kWh/year | 92248 | Annual energy consumption | kWh/year | 44
Implementation case |  |  | Implementation case |  |  | Implementation case |  |  | Implementation case
VFD frequency set | Hz | 44.25 | Water flow rate | m3/h | 29.2 | Water flow rate | m3/h | 42.5 | LED tube light rating | W | 21
Water flow rate | m3/h | 57.5025 | Power input | kW | 6.115 | Power input | kW | 6.543 | No. of lights | no's. | 3
Power input | kW | 23.0684 | Specific energy consumption | kWh/m3 | 0.20942 | Specific energy consumption | kWh/m3 | 0.15395 | Operating hours | hour/year | 250
Specific energy consumption | kWh/m3 | 0.40117 | Annual energy consumption | kWh/year | 53506.25 | Annual energy consumption | kWh/year | 57316.68 | Annual energy consumption | kWh/year | 15.75
Annual energy consumption | kWh/year | 218235.5784 | Energy saving | kWh/year | 10615.0496 | Energy saving | kWh/year | 34931.32 | Energy saving | kWh/year | 28.25
Energy saving | kWh/year | 105552.4216 | KPI improvement | % | 33.1588 | KPI improvement | % | 44.6509 | KPI improvement | % | 64.2045
KPI improvement | % | 35.0724 | GHG emission reduction | tCO2-e | 7.0059 | GHG emission reduction | tCO2-e | 23.0547 | GHG emission reduction | tCO2-e | 0.018645
GHG emission reduction | tCO2-e | 69.6646

## Tuvaruhu SIWA PS
Tuvaruhu SIWA Pump Station
ECM-1: Replacement of transfer pump-1 with IE4 motor & VFD |  |  | ECM-1: Replacement of transfer pump-2 with IE4 motor & VFD |  |  | ECM-2: Replacement of borepump-4 with efficient pump |  |  | ECM-3: Replacement of FTL with LED tube lights
Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value | Particular | Unit | Value
Baseline |  |  | Baseline |  |  | Baseline |  |  | Baseline
Operating flow | m3/h | 64.6 | Operating flow | m3/h | 62.9 | Operating flow | m3/h | 42.2 | FTL light rating | W | 36
Discharge head | m | 46 | Discharge head | m | 46 | Overall head | m | 30 | Ballast rating | W | 8
Power input | kW | 16.39 | Power input | kW | 16.78 | Power input | kW | 11.77 | Number of lights | no's. | 5
Net daily water duty | m3 | 707.8 | Net daily water duty | m3 | 707.8 | Net daily water duty | m3 | 1192 | Total rating | kW | 1.056
Specific energy consumption | kWh/m3 | 0.25372 | Specific energy consumption | kWh/m3 | 0.26677 | Specific energy consumption | kWh/m3 | 0.27891 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 65478 | Annual energy consumption | kWh/year | 67070 | Annual energy consumption | kWh/year | 99911 | Annual energy consumption | kWh/year | 55
Implementation case |  |  | Implementation case |  |  | Implementation case |  |  | Implementation case
VFD frequency set | Hz | 43.9 | VFD frequency set | Hz | 43.9 | Water flow rate | m3/h | 49.7 | LED tube light rating | W | 21
Water flow rate | m3/h | 57.1444 | Water flow rate | m3/h | 57.1444 | Power input | kW | 7.717 | No. of lights | no's. | 4
Power input | kW | 10.7929 | Power input | kW | 10.7929 | Specific energy consumption | kWh/m3 | 0.15527 | Operating hours | hour/year | 250
Specific energy consumption | kWh/m3 | 0.18887 | Specific energy consumption | kWh/m3 | 0.18887 | Annual energy consumption | kWh/year | 67555.5807 | Annual energy consumption | kWh/year | 21
Annual energy consumption | kWh/year | 48794.1156 | Annual energy consumption | kWh/year | 48794.1156 | Energy saving | kWh/year | 32355.4193 | Energy saving | kWh/year | 34
Energy saving | kWh/year | 16683.8844 | Energy saving | kWh/year | 18275.8844 | KPI improvement | % | 44.3291 | KPI improvement | % | 61.8182
KPI improvement | % | 25.5581 | KPI improvement | % | 29.2017 | GHG emission reduction | tCO2-e | 21.3546 | GHG emission reduction | tCO2-e | 0.02244
GHG emission reduction | tCO2-e | 11.0114 | GHG emission reduction | tCO2-e | 12.0621

## Kwaibala PS
Kwaibala Pump Station
ECM-1: Replacement of transfer pump |  |  | ECM-2: Replacement of FTL with LED tube lights
Particular | Unit | Value | Particular | Unit | Value
Baseline |  |  | Baseline
Operating flow | m3/h | 23.8 | FTL light rating | W | 36
Discharge head | m | 50 | Ballast rating | W | 8
Power input | kW | 8.09 | Number of lights | no's. | 6
Net daily water duty | m3 | 571.2 | Total rating | kW | 1.056
Specific energy consumption | kWh/m3 | 0.33992 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 70873 | Annual energy consumption | kWh/year | 66
Implementation case |  |  | Implementation case
Water flow rate | m3/h | 50 | LED tube light rating | W | 21
Power input | kW | 10.79 | No. of lights | no's. | 4
Specific energy consumption | kWh/m3 | 0.2158 | Operating hours | hour/year | 250
Annual energy consumption | kWh/year | 44991.7104 | Annual energy consumption | kWh/year | 21
Energy saving | kWh/year | 25881.2896 | Energy saving | kWh/year | 45
KPI improvement | % | 36.5137 | KPI improvement | % | 68.1818
GHG emission reduction | tCO2-e | 17.0817 | GHG emission reduction | tCO2-e | 0.0297