## Instructions
Instructions
1 | The model sheet covers:
(a) performance assessment of transfer pump, borepump, VFD, lighting system
(b) self-generation assessment - rooftop solar potential
(c) GHG emission estimation (Based on 2019 grid emission factor)
(d) Financial analysis of energy saving recommendation
2 | The user is recommended to fill data in only the light green highlighted cells
3 | Other cells are locked and can't be accessed by the user
4 | Please note the GHG emission factor changes annually based on generation mix.

## Transfer Pumps
Transfer pumps
| Design Details of Pumps |  |  | Design Details of Motors
| Particular | Unit | Pump 1 | Particular | Unit | Motor 1
| Make | - | Grundfos | Make | - | Groundfos
| Model | - | CRN 64-2-1 AFGV-HQQV | Power | kW | 11
| Design flow | m3/h | 64 | Voltage | V | 415
| Design head | m | 37.2 | Current | I | 19.8
| Max. head | m | 51.3 | Power Factor | - | 0.89
| Pump speed | rpm | 2924 | Motor speed | rpm | 2950
| Recommeded motor rating | kW | 11 | Frequency | Hz | 50
| Max. pressure | bar | 16 | Rating | - | IE3
| Pump efficiency | % | 77.1 | Efficiency | % | 91.2
| Operating Parameters Pumps |  |  | Operating Parameters Motors
| Particular | Unit | Pump 1 | Particular | Unit | Motor 1
| Operating flow | m3/h | 34.3 | Voltage | V | 436
| Suction head | m | -1 | Current | I | 14.5
| Discharge head | m | 34 | Power factor | - | 0.64
| Hydraulic power | kW | 3.0844 | Power input | kW | 7.0078
| Shaft power | kW | 6.3911 | Motor Efficiency | % | 91.2
| Pump efficiency | % | 48.2611 | Power shaft | kW | 6.3911
| Combined pump-motor eff. | % | 44.0141 | Motor loading | % | 58.1011

## VFD
Transfer pumps
| Design Details of Pumps |  |  |  | Design Details of Motors
| Particular | Unit | Pump 1 |  | Particular | Unit | Motor 1
| Make | - | Grundfos |  | Make | - | Groundfos
| Model | - | CRN 64-2-1 |  | Power | kW | 11
| Design flow | m3/h | 64 |  | Voltage | V | 415
| Design head | m | 37.2 |  | Current | I | 19.8
| Max. head | m | 51.3 |  | Power Factor | - | 0.89
| Pump speed | rpm | 2924 |  | Motor speed | rpm | 2950
| Recommeded motor rating | kW | 11 |  | Frequency | Hz | 50
| Max. pressure | bar | 16 |  | Rating | - | IE3
| Pump efficiency | % | 77.1 |  | Efficiency | % | 91.2
[5 empty] | Poles | no. | 2
Operating parameters
| Parameter | Unit | Design | Proposed
| N - Speed | rpm | 2950 | 2655
| F - Frequency | Hz | 50 | 44.25
| Q - Flow | m3/hr | 64 | 57.6
| H - Head | m | 37.2 | 30.132
| P - Power | kW | 7.1137 | 5.4452

## Borepump
Borepumps
| Design Details of Borewell Pumps |  |  | Design Details of Motors
| Particular | Unit | Borepump 1 | Particular | Unit | Motor 1
| Make | - |  | Make | -
| Model | - |  | Power | kW | 7.5
| Design flow | m3/h |  | Voltage | V | 415
| Design head | m |  | Current | I
| Max. head | m |  | Power Factor | -
| Pump speed | rpm |  | Motor speed | rpm
| Recommeded motor rating | kW |  | Frequency | Hz | 50
| Max. pressure | bar |  | Rating | - | NA
| Max. temperature | °C |  | Efficiency | % | 79.4
| Operating Parameters Borewell Pumps |  |  | Operating Parameters Motors
| Particular | Unit | Borepump 1 | Particular | Unit | Motor 1
| Operating flow | m3/h | 24.4 | Voltage | V | 433.4
| Well depth to water level | m | 35.6 | Current | I | 8.1
| Head from surface to resorvior | m | 4.3 | Power factor | - | 0.79
| Hydraulic power | kW | 2.653 | Power input | kW | 4.8034
| Shaft power | kW | 3.8139 | Motor Efficiency | % | 79.4
| Pump efficiency | % | 69.56 | Power shaft | kW | 3.8139
| Combined pump-motor eff. | % | 55.2307

## Lighting
Lighting
| Particular | Unit | Existing | Proposed
| Type | - | FTL T8 | LED
| Rating | W | 36 | 21
| Ballast rating | W | 8 | 0
| No. of lights | no. | 24 | 12
| Total rating | W | 1056 | 252
| Operating hours | hr/yr | 250 | 250
| Annual consumption | kWh/yr | 264 | 63
| Annual saving | kWh/yr |  | 201
| Monetary saving | SBD/yr |  | 1101.48
|  | USD/yr |  | 136.68
| Investment cost | USD |  | 240
| Simple payback | years |  | 1.7559
Note on E12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Electricity charges for 2019
Note on E13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Electricity charges for 2019

## Self-generation
Self Generation options
Honiara Average Solar Radiation Data (kWh/m2/day)
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Avg | Particular | Unit | Thin-film | Monocrystalline
Solar Radiation Data (kWh/m2/day) | 5.25 | 4.99 | 5.05 | 4.91 | 4.39 | 4.19 | 4.12 | 4.67 | 5.21 | 5.67 | 5.64 | 5.35 | 4.9533 | Available roof area | m2 | 160 | 160
Average | 4.9533 | 4.9533 | 4.9533 | 4.9533 | 4.9533 | 4.9533 | 4.9533 | 4.9533 | 4.9533 | 4.9533 | 4.9533 | 4.9533 |  | Utilization area | m2 | 136 | 136
[14 empty] | Nominal power | kWp | 13.6 | 21.7949
[14 empty] | Average global horizontal irradiance | kWh/m2/day | 4.95 | 4.95
[14 empty] | Proposed tilt angle | degree | 10 | 10
[14 empty] | Annual solar yield | kWh/year | 24571.8 | 39377.8846
[14 empty] | Avg fuel charges | SBD/kWh | 2.65 | 2.65
[14 empty] | Monetary saving | SBD/year | 65115.27 | 104351.3942
[15 empty] | USD/year | 8139.4087 | 13043.9243
[14 empty] | Module cost | USD | 12716 | 20346
[14 empty] | Supports cost | USD | 15558 | 15558
[14 empty] | Inverter and wiring cost | USD | 4787 | 4787
[14 empty] | Transport and mounting cost | USD | 18370 | 26755
[14 empty] | Cost at port in Solomon Islands | USD | 51431 | 67446
[14 empty] | Import duty | % | 10 | 10
[14 empty] | GST on imported goods | % | 15 | 15
[14 empty] | Net landed cost | USD | 64913.75 | 84932.5
[14 empty] | Simple payback period | years | 7.9752 | 6.5113
Note on R11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These costs are typical for January 2020

## GHG emission factor
GHG emmisions
Grid Emission Factor | 0.66 | tCO2/MWh | Source: http://documents.worldbank.org/curated/en/772871531020654750/pdf/Solomon-Islands-Electricity-PAD-06132018.pdf
Annual energy saving | 40557
Annual GHG emissions reduction | 26.7676
Note on B3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: grid emission factor for 2019

## Financial Analysis
Financial Analysis
| Financial Analysis |  |  |  |  | Simple Payback | 2.6667 | Years
| Rate | 10% | Project Life | 10 | Yrs | NPV | 26084.2533 | US$ | 23192.6786 | -3192.6786 | -1.1041
| Year | Discount Factor | Net cashflow | Discounted cash flow | NPV | IRR | 35.73%
| 0 | 1 | -20000 | -20000 | -20000 | RoI | 37.5%
| 1 | 0.90909 | 7500 | 6818.1818 | -13181.8182
| 2 | 0.82645 | 7500 | 6198.3471 | -6983.4711
| 3 | 0.75131 | 7500 | 5634.861 | -1348.6101
| 4 | 0.68301 | 7500 | 5122.6009 | 3773.9908
| 5 | 0.62092 | 7500 | 4656.9099 | 8430.9008
| 6 | 0.56447 | 7500 | 4233.5545 | 12664.4552
| 7 | 0.51316 | 7500 | 3848.6859 | 16513.1411
| 8 | 0.46651 | 7500 | 3498.8054 | 20011.9465
| 9 | 0.4241 | 7500 | 3180.7321 | 23192.6786
| 10 | 0.38554 | 7500 | 2891.5747 | 26084.2533
| Total |  |  | 26084.2533
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capital cost to be entered in negative
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Energy cost escalation to be incorporated